Why use a UPS ?

There are at least 3 good reasons

third reason:  to be  independent from extern influences  !

A reliable powersupply system means often a lot more than the quality provided by the local electricy board .

Certain Industrial  processes react very  sensitive on decreasing mains supply quality.

- Hospitals

- Airports

- Semi conductor production plants

- Chemical Industry/ plastics technology

- Electronic dataprocessing centers

- Telecommunication

- Computer controlled Industrial plants etc.

first of all:   to save money !

mains failure of as a little as a millisecond will cause serious consquences   and  expensive   production outage and subsequent mistake costs in a wide range of industrial,  electronical, airports, computer  centers  and  healthcare  applications.

second reason:  to prevent standstill of production !

Increasing degree of automation in modern production processes demands more than ever an absolute reliable and uninterrupted mains supply to prevent standstill and production losses .

„ What kind of UPS -System?“

UPS- System  is the solution !

A Dynamic Uninterrupted Power supply- system from

is the solution for quality problems in mains supply of your organisation.

A                     - UPS System is  taylormade regarding to your very

special situation and enables a  return of investment during a very short time.

- Ratings: up to 2000kva

- Voltage up to 11 kv

- MTBF value: 20 years

- Low  maintenance costs

- High alternator efficiency

We are sure to find the best state of the art solution at an affordable price

also for your application, with our  No-Break Systems   NBDD & NBDK .

The             - UPS Systems enable you to reduce

production outages and prevent financial losses.

- Power factor improvement

- High quality of components

- High overload capability

- Optimum mains failure supervision

- In house developed PLC control system

NBDK  UPS- System Technical Details

Static     :      + 1 %

Dynamic: a) at nominal  load change, cos-phi = 0,8,:    +10  %

recovery time 0,3 sec

b)  during short circuit on incoming feeder + 10 %. The voltage tolerance

after switching off the short circuit is less than10 % recovery time 0,3 sec.

c)  When switching off the incoming supply at nominal voltage + 10 %

and a recovery time of 0,3 sec.

Power: 100 – 2000 kVA

Voltage:          up to 11 kV

Frequency:        50/60 Hz

Guaranteed Tolerances

Voltage

Frequency

Other tolerances / specifications are available on demand

a)   during mains operation = mains frequency

b)  changing from mains to diesel engine operation and an active load of 100 %       + 1 %

c)  statical - during diesel engine operation + 0,5 %.

NBDK Function

During stand-by operation consumers and the synchronous machine are both supplied via the choke from the mains. Consumer frequency is equal to the mains frequency. Synchronous machine maintains consumer voltage constant, irrespective of the mains voltage fluctuations and supplies most of the reactive power of the consumers.

The power factor on mains input is approx. 1.

Unsymmetric consumer current is shared from choke and synchronous machine symmetrically on all three phases on the mains input.

Consumers harmonics back to mains are largely filtered out.

In the event of mains failure, mains circuit breaker opens and consumers are supplied temporarely from the KIN (kinetic energy storage module). The electromagnetic clutch is energized diesel engine accellerates  via highspeed-start to nominal speed.

The diesel engine becomes now the driving energy source and charges the KIN-Module again to be prepared for the next mains failure event.

On mains restoration, the consumers are back synchronized after a certain time delay period. Clutch opens and diesel engine is shut off after adjusted cooling down period.

A frame mounted radiator and an external electrical driven fan  is used for Hitzinger NBDK´s. It ensures to eliminate radiated waste heat during stand-by operation as well as to cool the engine during mains failure periods when the diesel engine is in operation.

To shut down the NBDK system, the diesel engine is started and consumers are supplied via the by-pass circuit breaker which is synchonized to mains. Both CB´s (mains and alternator) are switched off and the machinery decelerates and shuts down.

Putting into operation is performed vice versa.

NBDK – Schematic diagram

Mains supply

14

15

16

17

12

11

7

8

10

9

1

3

6

4

18

Consumer voltage

18.clean power

By-Pass operation

Stand By-operation

Dieseloperation

Frequency drop = 1 %

13

14 Harmonic distortion

15 Voltage ipulse

16 Voltage drop

17 Outage

9    Costumer circuit breaker

10  Alternator circuit breaker

11  By-Pass- circuit breakerr

12  Mains input

13  Consumer Output

1  Diesel engine

3  Electromagnetic clutch

6  Synchronous machine

4  Kinetic module

7  Choke

8  Mains-circuit breaker

Power:  100 – 2000 kVA

Voltage:           up to 11 kV

Frequency:           50/60 Hz

NBDK – Combi  Technical details

Guaranteed Tolerances:

Voltage

Static     :      + 1%

Dynamic: a) at nominal  load change, cos-phi = 0,8,:    +10  %

recovery time 0,3 sec

b)  during short circuit on incoming feeder + 10 %. The voltage tolerance

after switching off the short circuit is less than10 % recovery time 0,3 sec.

c)  When switching off the incoming supply at nominal voltage + 10 %

and a recovery time of  0,3 sec.

Frequency

c)  statical - during diesel engine operation + 0,5 %.

b)  changing from mains to diesel engine operation and an active load of 100 %       + 1 %

Other tolerances / specifications available on demand

a)   during mains operation = mains frequency

NBDK - Combi  function

HITZINGER has developed the NBDK Combi  system to maintain  critical loads and non-critical loads within one system.

This system provides the consumer the quality and continuity of electrical power which is required for UPS load and Emergency Power Supply as well

6

4

2

1

1  diesel engine

2  electromagnetic clutch

4  synchronous motor /alternator

6  kinetic module

Description of operation

During mains operation ( stand by mode) consumers and synchronous machine are both supplied via the choke from the mains and the kinetic module is fully charged.

This construction acts as a stabilizing filter and provides clean regulated power to the critical load.

The emergency consumers ( non critical load) are directly supplied form the mains.
In case of mains failure, mains circuit breaker opens and consumers are supplied without any interruption temporary from the kinetic module.

The diesel is started , the electromagnetic clutch is energized bevore engine reaches its nominal speed.

The diesel engine and the unit supply continousely the  critical loads ( Frequency drop <= 1%).

A few seconds later when  the diesel has reached nominal speed and the kinetic Module is charged again, the non-critical loads are connected to the system

NBDK - Combi  Schematic diagram

7

1000

1555

1121

8

9

16

1434

13

1

3

4

6

1  diesel engine

3  electromagnetic clutch

4  synchronous motor /alternator

6  kinetic module

7  choke

8  mains circuit breaker

9  consumer circuit breaker

10  alternator circuit breaker

11  by-pass circuit breaker

12  mains input

13  consumer outlet UPS

14  consumer outlet EPS

15  by-bass circuit breaker II

16  alternator circuit breaker II