#### Selection of EPS

with

interruption

without

interruption

Selection of

### Emergency Power Supply Systems

Hitzinger  UPS

Type NBDD 1000 kVA

Hitzinger  Short break

Type CSBG  450 kVA

Emergency Power Supply
with interruption

generating

set system

rotary short

break system

Combined short break /

generating set system

no energy storage

flywheel

energy storage

flywheel

energy storage

GEN SET

SBDS / SBDA

CSBG

A

15 s

300 ms

- genset mode :  + 15 s

- short break mode   : 300 ms

B

+ 10 %

- genset mode : + 10 %

- short break mode   : + 10 %

C

+ 8 %

+5%/+5% (adjustable)

- genset mode : + 8 %

- short break mode   : +5%(adj.)

+ 20 %

On special request other tolerances are available !

A : interruption time in case of mains failure

B : voltage transient for dynamic load step and switching from normal to emergency operation

C : frequency transient for dynamic load step and switching from normal to emergency operation

No Break Generating Sets

Emergency Power Supply

without interruption

A

B

C

NBDD

NBDK

0

0

+ 10 %

+ 10 %

+ 5 %

+ 1 %

A: interruption time in case of mains failure

B: voltage transient for dynamic load step and switching from normal to emergency operation

C: frequency transient for dynamic load step and switching from normal to emergency operation

dynamic UPS System

dynamic UPS System

kinetic

energy module

flywheel

energy storage

On special request other tolerances are available !