[BASLER ELECTRIC BE1-700 Guideform Specification]

This specification describes requirements for a numeric multifunction Overcurrent Protection System (communicating microprocessor-based relay). The relay system shall have a 7-year warranty. The relay system shall provide protection, monitoring, control, and standard automation protocols [OPTION: and an internal Ethernet port for status, metering, and configuration]. Relay self-checking functions shall be included. Specific requirements are as follows:

# OVERCURRENT PROTECTION:

Phase Faults   (50/51P, 50/51Q) The relay shall include 2 phase and 2 negative sequence instantaneous overcurrent elements, and 1 phase and 1 negative sequence time overcurrent element for detecting phase faults. Each instantaneous element shall have an adjustable definite time delay.

Ground Faults (50/51N) The relay shall include 2 neutral instantaneous overcurrent elements and 2 neutral time overcurrent elements that can be selected by setting to operate on either calculated residual (3I0) current or the independent ground current input for detection of ground faults. Each instantaneous element shall have an adjustable definite time delay.

# SENSING AND CONTROL:

[OPTION: Automatic Reclosing Control (79) The relay shall be capable of 4 reclosing attempts. The first reclose shall be user-selectable as a stand-alone pilot initiated reclose or included as part of a standard 4 shot recloser, driven by a separate reclose initiate. Zone sequence coordination and sequence controlled protective element blocking functions shall also be included. The element shall include independent reclose timers for pilot and up to three additional time delay recloses, a timer for reset after a successful reclose, maximum cycle timer, and reclose fail timer.]

Setting Groups The relay shall have 2 user-programmable settings groups.

Input/Output The relay shall have 4 optically isolated inputs, 5 general purpose output contacts, and one fail-safe normally closed alarm output contact. Each output shall be isolated and rated for tripping duty (30 A for 0.2 seconds, 7 A continuous).

Virtual Control Switches (43/101) The relay shall include 2 virtual selector switches (x43) and a virtual breaker control switch (101), controllable from both the HMI and communication ports.

Relay Logic The relay shall include programmable logic for each output, for all inputs, and at least ten additional logic equations for user programming.

Logic Timers and Logic Latches (62) The relay shall include 2 logic timers (62) to aid in the development of custom logic.

Terminal Blocks and Wiring Other than RS-232 wiring, all connections, including RS-485 wiring and IRIG-B wiring, shall be to barrier terminal strips capable of accepting ring lug connection. RS-232 wiring shall be to a DB9S female connector on the front of the relay. RS-232 wiring shall be configured to allow 1-to-1 wiring to the DTE port on a PC, without need for null-modem adaptors or proprietary cabling or connectors. [OPTON: Ethernet connection shall be via standard RJ-45 10/100BaseT connector internal to the relay and located on the rear panel. External serial to Ethernet converters or adapters are not acceptable.]

HMI/ DISPLAY A backlit 2 line x 16-character LCD display shall be provided integral to the relay, along with a 4 key cursor/navigation keypad. Separate target/alarm reset and settings edit pushbuttons shall be included. Keypad/pushbuttons shall include a continuous, flexible membrane overlay over all keys.

# REPORTING AND ALARMS:

Oscillography and Sequential Events Recorder (SER) The relay shall be capable of automatically recording disturbance events of 15 to 40 cycles (user-adjustable), with 4 cycles of prefault duration and user-defined triggering. The relay shall include a Sequence of Events Recording function (SER) that stores the latest 255 events.

Nonvolatile Status and Trip Target LEDs The relay shall hold all programmed target and alarm information in nonvolatile memory and shall provide that information locally through the HMI/LEDs, and remotely via communication ports. Relay shall have three programmable alarm bits: Major, Minor, and Logic, based upon relay logic states.

Real Time Metering The relay shall include real time metering that provides Phase, Neutral, and Negative Sequence amp, and unbalance loading telemetry for the protected circuit.

Demand Metering The relay shall include user-settable current demands for phase, neutral, and negative sequence currents with magnitudes and time stamps recorded for today's peak, yesterday's peak, and peak since reset.

Circuit Breaker Monitor The relay shall include breaker status and operations counter reporting, fault current interruption duty monitoring (must include user-settable exponent for In), and trip-speed monitoring. A trip coil monitor circuit shall be internally connected across the trip output to provide trip circuit continuity monitoring. No additional external wiring shall be required to implement the trip circuit monitor function.

# COMMUNICATIONS:

Relay Interface The relay shall include two independent general-purpose serial communication ports: a front RS-232 port and a rear RS-485 port. [OPTION: An internal, rear-panel accessible 10/100BaseT Ethernet port shall also be included.] [OPTON: All communications ports shall support ASCll protocol.] OR [The RS-485 port shall support Modbus™ protocol. Other port(s) shall support ASCII protocol.]

[OPTION: Modbus RTU Slave Communications The relay shall incorporate Modbus RTU slave protocol internally. External converters or adapters are not acceptable.]

[OPTION: Ethernet Communication features

The internal RJ-45 Ethernet port shall support the following functions:

- Internal Web Server providing metering and status information and access to fault summary reports. Metering web page shall allow a static snapshot mode or a continuously updating ‘live’ mode.

- Email alerts that automatically send an email message when a user-programmed logic condition occurs. The relay shall allow at least 5 different logic conditions to be defined simultaneously, and each logic condition shall allow a different send-to email address and cc email address to be entered

- ASCII over TCP communications for settings entry and oscillography file retrieval. User-friendly PC software capable of communication over Ethernet shall be included at no charge. Additional copies of this software must be available at no charge for use by end user.

IRIG-B The relay shall include an interface port for a demodulated IRIG-B time synchronization input signal. IRIG-B connection shall be to a barrier terminal strip capable of accepting ring lug terminated wiring.

PC Interface The relay shall be capable of being set through the front panel RS-232 port by Windows®-based graphical user interface software and ASCII terminal interfaces.

# SETTINGS AND ANALYSIS SOFTWARE:

# PC Software:  PC Software compatible with Windows 98, NT, 2000, XP Home, XP Professional, and Windows Me shall be included at no charge. The software shall be freely reproducible within the end user’s organization without additional charge. The software must include serial [OPTION: and Ethernet] communications for settings upload and download, graphical programming and display of logic equations (including pictorial display of AND and OR gates), and the ability to display and print COMTRADE oscillography and event files.

# CASE OPTIONS (packaging):

Half 19” Rack or Panel Mount (H1 Case) The relay shall be packaged in a flush panel-mounted case no larger than 10.5” wide, 4.5” high, 8” deep behind the panel face (including rear termination blocks), and projecting no more than 3/8” in front of the mounting surface (inclusive of any front panel connectors, covers, handles, etc.).