Note: Items in blue indicate optional or Basler specific items. Some options are mutually exclusive (only one can be selected). After deleting options that are not required, blue text should be removed to create a generic specification.

[BASLER ELECTRIC BE1-700V Voltage/Frequency Relay Guideform Specification]

This specification describes requirements for a numeric multifunction Voltage/Frequency Protection System (communicating microprocessor-based relay). The relay system shall have a 7-year warranty. The relay system shall provide protection, monitoring, control, and standard automation protocols [OPTION: and an internal Ethernet port for status, metering, and configuration]. Relay self-checking functions shall be included. Specific requirements are as follows:

# VOLTAGE PROTECTION:

Volts per Hertz Overexcitation (24) The relay shall include a volts/hertz protection element to protect against transformer and generator overexcitation conditions.

Phase Under/Overvoltage (27P/59P) The relay shall include 2 phase undervoltage and 2 phase overvoltage elements for detecting single or multiphase voltage events. Each voltage element shall be independently configurable for “1 of 3”, “2 of 3” or “3 of 3” phase operation and settable to monitor either ph-ph or ph-n voltages. The 27P elements shall have an undervoltage inhibit setting, with a setting range of 1 to 150Vac.

Auxiliary Under/Overvoltage (27X/59X) The relay shall include 1 under and 2 overvoltage elements that monitor phase residual voltage (3V0) for detecting grounds on a delta system, or monitors [OPTION: auxiliary voltage input or] an external broken delta VT source or a neutral voltage source (capacitor bank or generator) for detecting ground faults. Elements shall monitor either fundamental or third harmonic values.

Negative Sequence Overvoltage (47) The relay shall include a negative sequence voltage element for detecting phase unbalance and reverse phase rotation.

Fuse Loss Detection (60) The relay shall include a fuse loss detection element (sensing voltage input) that protects against false tripping for a blown sensing fuse.

Under/Over Frequency (81O/U) The relay shall include 6 frequency elements (settable for over or under frequency detection) for detection of power system frequency disturbances. Each of the frequency elements shall have independently set timers. The frequency elements shall have a common undervoltage inhibit setting.

# SENSING AND CONTROL:

[OPTION : Automatic Reclosing Control (79) The relay shall be capable of 4 reclosing attempts. The first reclose shall be user-selectable as a stand-alone pilot initiated reclose or included as part of a standard 4 shot recloser, driven by a separate reclose initiate. Zone sequence coordination and sequence controlled protective element blocking functions shall also be included. The element shall include independent reclose timers for pilot and up to three additional time delay recloses, a timer for reset after a successful reclose, maximum cycle timer, and reclose fail timer.]

[OPTION: Synchronism Check (25) An optional auxiliary voltage input can be connected for synch check protection. This protection shall check for phase angle difference, voltage magnitude difference, frequency difference (slip) and if the 3-phase VT source voltage frequency is greater than the auxiliary VT frequency. A voltage monitor output shall provide independent dead/live voltage closing logic.]

Setting Groups The relay shall have two user programmable settings groups.

Input/Output The relay shall have 4 optically isolated inputs, 5 general purpose output contacts, and one fail-safe normally closed alarm output contact. Each output shall be isolated and rated for tripping duty (30 A for 0.2 seconds, 7 A continuous).

Virtual Control Switches (43/101) The relay shall include two virtual selector switches (x43) and a virtual breaker control switch (101), controllable from both the HMI and communication ports.

Relay Logic The relay shall include programmable logic for each output, for all inputs, and at least ten additional logic equations for user programming.

Logic Timers (62/162) The relay shall include two logic timers (62/162) to aid in the development of custom logic.

Selectable Wye or Delta Voltage Inputs The relay shall be field selectable after purchase to operate with either wye-connected (four wire) or open-delta-connected (three wire) potential transformers.

Terminal Blocks and Wiring Other than RS-232 wiring, all connections, including RS-485 wiring and IRIG-B wiring, shall be to barrier terminal strips capable of accepting ring lug connection. RS-232 wiring shall be to a DB9S female connector on the front of the relay. RS-232 wiring shall be configured to allow 1-to-1 wiring to the DTE port on a PC, without need for null-modem adaptors or proprietary cabling or connectors.

HMI/ DISPLAY A backlit 2 line x 16-character LCD display shall be provided integral to the relay, along with a 4 key cursor/navigation keypad. Separate target/alarm reset and settings edit pushbuttons shall be included. Keypad/pushbuttons shall include a continuous, flexible membrane overlay over all keys.

# REPORTING AND ALARMS:

Oscillography and Sequential Events Recorder (SER) The relay shall be capable of automatically recording disturbance events of 15 to 40 cycles (user adjustable), with 4 cycles of prefault duration and user defined triggering. The relay shall include a Sequence of Events Recording function (SER) that stores the latest 255 events.

Non-Volatile Status and Trip Target LEDs The relay shall hold all programmed target and alarm information in non-volatile memory and provide that information locally through the HMI/LED’s, and remotely via communication ports.

Real Time Metering The relay shall include real time metering that provides p-n and p-p voltage, zero and negative sequence voltage, frequency, and slip angle for the optional 25 function.

Circuit Breaker Monitor The relay shall include a breaker operations counter for reporting purposes. A trip coil monitor circuit shall be internally connected across the trip output to provide trip circuit continuity monitoring. No additional external wiring shall be required to implement the trip circuit monitor function.

# COMMUNICATIONS:

[Select one of the following]

[OPTION No Ethernet, ASCII RS485

The relay shall include two independent general-purpose serial communication ports: a front RS-232 port and a rear RS-485 port. All communications ports shall support ASCll protocol. ]

[OPTION No Ethernet, Modbus/RTU RS485

The relay shall include two independent general-purpose serial communication ports: a front RS-232 port supporting ASCII communications, and a rear RS-485 port support Modbus/RTU Slave protocol. The relay shall incorporate Modbus RTU slave protocol internally. External converters or adapters are not acceptable.]

[OPTION BESTNET Ethernet, ASCII RS485

Relay Interface The relay shall include three independent communication ports: a front RS-232 port, a rear RS-485 port, and an internal, rear-panel accessible 10/100BaseT Ethernet port. All communications ports shall support ASCll protocol.

Ethernet Communication features

The internal RJ-45 Ethernet port shall support the following functions:

- Internal Web Server providing metering and status information and access to fault summary reports. Metering web page shall allow a static snapshot mode or a continuously updating ‘live’ mode.

- Email alerts that automatically send an email message when a user-programmed logic condition occurs. The relay shall allow at least 5 different logic conditions to be defined simultaneously, and each logic condition shall allow a different send-to email address and cc email address to be entered

- ASCII over TCP communications for settings entry and oscillography file retrieval. User-friendly PC software capable of communication over Ethernet shall be included at no charge. Additional copies of this software must be available at no charge for use by end user.]

[OPTION BESTNET Ethernet, Modbus RS485

Relay Interface The relay shall include three independent communication ports: a front RS-232 port, a rear RS-485 port, and an internal, rear-panel accessible 10/100BaseT Ethernet port. The RS-485 port shall support Modbus/RTU Slave protocol. The relay shall incorporate Modbus RTU slave protocol internally. External converters or adapters are not acceptable. Other port(s) shall support ASCII protocol.

Ethernet Communication features

The internal RJ-45 Ethernet port shall support the following functions:

- Internal Web Server providing metering and status information and access to fault summary reports. Metering web page shall allow a static snapshot mode or a continuously updating ‘live’ mode.

- Email alerts that automatically send an email message when a user-programmed logic condition occurs. The relay shall allow at least 5 different logic conditions to be defined simultaneously, and each logic condition shall allow a different send-to email address and cc email address to be entered

- ASCII over TCP communications for settings entry and oscillography file retrieval. User-friendly PC software capable of communication over Ethernet shall be included at no charge. Additional copies of this software must be available at no charge for use by end user. ]

[OPTION Modbus/TCP Ethernet, ASCII RS485

Relay Interface The relay shall include three independent communication ports: a front RS-232 port, a rear RS-485 port, and an internal, rear-panel accessible 10/100BaseT Ethernet port. The relay shall incorporate true Modbus/TCP Ethernet protocol internally. External converters or adapters are not acceptable, nor are simple TCP/IP tunnels for Modbus/RTU protocol. Other ports shall support ASCII protocol.]

IRIG-B The relay shall include an interface port for a demodulated IRIG-B time synchronization input signal. IRIG-B connection shall be to a barrier terminal strip capable of accepting ring lug terminated wiring.

PC Interface The relay shall be capable of being set through the front panel RS-232 port by Windows®-based graphical user interface software and ASCII terminal interfaces.

# SETTINGS AND ANALYSIS SOFTWARE:

# PC Software:  PC Software compatible with Windows 98, NT, 2000, XP Home, XP Professional, and Windows Me shall be included at no charge. The software shall be freely reproducible within the end user’s organization without additional charge. The software must include communications to the relay for settings upload and download, graphical programming and display of logic equations (including pictorial display of AND and OR gates), and the ability to display and print COMTRADE oscillography and event files.

# CASE:

Panel Mount The relay shall be packaged in a flush panel-mounted case no larger than 10.5” wide, 4.5” high, 8” deep behind the panel face (including rear termination blocks), and projecting no more than 3/8” in front of the mounting surface.