## Instructions
Basler Electric
Time Dial Calculator Rev. A
Disclaimer
This spreadsheet presents information about Basler Electric relays. It has been
prepared as a convenience to our customers, and there is no expressed or
implied commitment to maintain or update this file. In developing this
software, Basler has attempted to offer the most accurate information possible.
Basler does not warrant that the software is free from bugs, errors or other
program limitations. Users are encouraged to consult with a Basler Electric
representative to determine the accuracy of the data and results for the specific
use or purpose of the user.
The spreadsheet is protected to prevent accidental erasure of data. It is not
password protected, to enable the user to modify it or to customize if for the
user own purposes.
By use of this program, the user agrees that Basler disclaims all warranties of
noninfringement of third party rights, quality, performance, merchantability, or
fitness for a particular purpose. The user assumes the entire risk as to the
quality and performance of the software. In no event will Basler be liable for
any indirect, special or consequential damages.
In the event of any litigation regarding this software, the user agrees that venue
shall be in the State of Illinois.
Purpose of this Spreadsheet
Basler Electric inverse time overcurrent relays (ANSI Device 51) provide
time/current characteristic curves that very closely emulate most of the
common electro-mechanical, induction disk relays that were manufactured in
North America. To further improve proper relay coordination, selection of
integrated reset or instantaneous reset characteristics is also provided in most
Basler Electric relays.
Even though the TCC curve shapes have been optimized for each relay,
the time dial settings between electro-mechanical induction disk overcurrent
relays and Basler Electric relays are not equivalent. This spreadsheet has been
designed to serve as a tool for converting time dial settings for induction disk
relays to the correct equivalent time dial setting for your Basler Electric solid
state and numerical overcurrent relays. This tool applies to the following relays:
BE1-50/51B and 50/51M, CT powered overcurrent relays.
BE1-DFPR numerical multifunction feeder protection relay.
BE1-851 numerical multifunction overcurrent protection system.
BE3-GPR numerical multifunction generator protection system.
Note:
Note that all versions of the above listed products do not
necessarily provide all of the electro-mechanical curve
settings covered in this spreadsheet. Please consult the
appropriate bulletin or instruction manual for the capabilities
of each individual device.
This spreadsheet does not apply to the BE1-51 and 67 series relays.
How to Use this Tool
1. Find the tab of the workbook for the appropriate electro-mechanical relay
that you wish to emulate. Each tab provides a cross reference to the
appropriate Basler Electric curve setting, curve name, and TCC curve
drawing number. Westinghouse and ABB are equivalent.
2. If you have a time and multiple of tap test point that you have previously
calibrated the electro-mechanical relay to, simply enter these two values into
the appropriate fields. The nearest equivalent Basler Electric time dial
setting will be calculated for you.
3. If you have a time dial setting for the electro-mechanical overcurrent relay,
you may use the cross reference provided to obtain the nearest equivalent
Basler Electric time dial setting.
Notes
1. The values in the cross reference table were obtained by inspection of the
published electro-mechanical time current characteristic curve. The time
delay for each time dial setting at a current of five times tap was entered into
the time dial calculator function. The equivalent Basler Electric time dial
setting was then entered into the cross reference table.
2. If your electro-mechanical relay time dial setting is between the values
provided in the table, it will be necessary to interpolate (estimate the correct
intermediate value) between the electro-mechanical setting and the Basler
Electric setting.
3. The maximum time dial setting provided by Basler Electric relays is 9.9. The
Basler Electric equivalent time dial setting for the maximum time dial setting
provided in the electro-mechanical relay is provided in the cross reference
table even if it is calculated to be above 9.9. This is provided for the purpose
of allowing interpolation as noted above.
4. Basler Electric time/current characteristics are determined by a linear
mathematical equation. An induction disk has a certain degree of non-
linearity due to inertia and friction effects. For this reason, even though every
effort has been made to provide equation constants that provide
characteristic curves with minimum deviation from the published electro-
mechanical curves, slight deviations can be observed between them.
In applications where the time coordination between curves is extremely
close, we recommend that you choose the optimal time dial setting by
inspection of the coordination study. Also, in these applications where
coordination is tight, it is recommended that you retrofit your circuits with
Basler Electric solid state relays due to their high timing accuracy.
Revision Notes:
Versions of this spreadsheet dated earlier than 2/26/98 have incorrect data
for the Basler Electric S2 (GE IAC 55) curve. The B parameter for calculating
the time current characteristic of the BE S2 curve was incorrectly entered as
0.02800. The correct coefficient is 0.02080. The calculation of the time dial
settings that would provide equivalent timings to the GE curve were thus
in error making the cross reference table data for that curve incorrect.
Basler Electric Company, P.O. Box 269, Highland, Illinois USA 62249
Phone: 618/654-2341 l Fax: 618/654-2351 l Website: http://www.basler.com
Page Down To Purpose Description
Page Down To Instructions

## Cross Reference Table
This table applies to Time/Current Characteristic curves used in the BE1-DFPR,
the BE1-851, the BE3-GPR and the BE1-50/51 series relays.
The equivalent time dial settings were calculated at a value of five times pickup.
The valid time dial settings for Basler Electric inverse time overcurrent relays are 0.0 to 9.9.
Time Dial Setting Cross Reference Rev. A
Electromechanical Relay Time Dial Setting
|  |  | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Curve Name | Equivalent to | Drawing No. | Electromechanical Relay Time Dial Setting 0.5: Basler Electric Equivalent Time Dial Setting
S, Short Inverse | ABB CO-2 | 99-1369 | 0.3 | 0.8 | 1.7 | 2.4 | 3.4 | 4.2 | 5 | 5.8 | 6.7 | 7.7 | 8.6 | 9.7
L, Long Inverse | ABB CO-5 | 99-1370 | 0.4 | 0.8 | 1.5 | 2.3 | 3.3 | 4.2 | 5 | 6 | 7 | 7.8 | 8.8 | 9.9
D, Definite Time | ABB CO-6 | 99-1371 | 0.5 | 1.1 | 2 | 2.9 | 3.7 | 4.5 | 5 | 5.9 | 7.2 | 8 | 8.9 | 10.1
M, Moderately Inverse | ABB CO-7 | 99-1369 | 0.4 | 0.8 | 1.7 | 2.5 | 3.3 | 4.3 | 5.3 | 6.1 | 7 | 8 | 9 | 9.8
I, Inverse Time | ABB CO-8 | 99-1373 | 0.3 | 0.7 | 1.5 | 2.3 | 3.2 | 4 | 5 | 5.8 | 6.8 | 7.6 | 8.7 | 10
V, Very Inverse | ABB CO-9 | 99-1374 | 0.3 | 0.7 | 1.4 | 2.1 | 3 | 3.9 | 4.8 | 5.7 | 6.7 | 7.8 | 8.7 | 9.6
E, Extremely Inverse | ABB CO-11 | 99-1375 | 0.3 | 0.7 | 1.5 | 2.4 | 3.2 | 4.2 | 5 | 5.7 | 6.6 | 7.8 | 8.5 | 10.3
I2, Inverse Time | GE IAC-51 | 99-1597 | 0.6 | 1 | 1.9 | 2.7 | 3.7 | 4.8 | 5.7 | 6.8 | 8 | 9.3 | 10.6
V2, Very Inverse | GE IAC-53 | 99-1596 | 0.4 | 0.8 | 1.6 | 2.4 | 3.4 | 4.3 | 5.1 | 6.3 | 7.2 | 8.4 | 9.6
S2, Short Inverse | GE IAC-55 | 99-1595 | 0.2 | 1 | 2 | 3.1 | 4 | 4.9 | 6.1 | 7.2 | 8.1 | 8.9 | 9.8
L2, Long Inverse | GE IAC-66 | 99-1594 | 0.4 | 0.9 | 1.8 | 2.7 | 3.9 | 4.9 | 6.3 | 7.2 | 8.5 | 9.7 | 10.9
E2, Extremely Inverse | GE IAC-77 | 99-1598 | 0.5 | 1 | 1.9 | 2.7 | 3.5 | 4.3 | 5.2 | 6.2 | 7.4 | 8.2 | 9.9

## ABB CO-2
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-2
|  | BE1-851 Curve |  | S1
|  | Curve Name |  | S, Short Inverse
|  | Drawing No. |  | 99-1369
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
0.2663 | 0.03393 | 1 | 1.2969 | 0.028 | 0.332 | 5 | 4.2438
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | CO-2 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.3
|  |  | 1 | 0.8
|  |  | 2 | 1.7
|  |  | 3 | 2.4
|  |  | 4 | 3.4
|  |  | 5 | 4.2
|  |  | 6 | 5
|  |  | 7 | 5.8
|  |  | 8 | 6.7
|  |  | 9 | 7.7
|  |  | 10 | 8.6
|  |  | 11 | 9.7

## ABB CO-5
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-5
|  | BE1-851 Curve |  | L1
|  | Curve Name |  | L, Long Inverse
|  | Drawing No. |  | 99-1370
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
5.6143 | 2.1859 | 1 | 1 | 0.028 | 35.5 | 5 | 9.8822
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | CO-5 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.4
|  |  | 1 | 0.8
|  |  | 2 | 1.5
|  |  | 3 | 2.3
|  |  | 4 | 3.3
|  |  | 5 | 4.2
|  |  | 6 | 5
|  |  | 7 | 6
|  |  | 8 | 7
|  |  | 9 | 7.8
|  |  | 10 | 8.8
|  |  | 11 | 9.9

## ABB CO-6
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-6
|  | BE1-851 Curve |  | D
|  | Curve Name |  | D, Definite Time
|  | Drawing No. |  | 99-1371
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
0.4794 | 0.21359 | 1 | 1.5625 | 0.028 | 2.6 | 5 | 10.0556
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | CO-6 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.5
|  |  | 1 | 1.1
|  |  | 2 | 2
|  |  | 3 | 2.9
|  |  | 4 | 3.7
|  |  | 5 | 4.5
|  |  | 6 | 5.4
|  |  | 7 | 5.9
|  |  | 8 | 7.2
|  |  | 9 | 8
|  |  | 10 | 8.9
|  |  | 11 | 10.1

## ABB CO-7
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-7
|  | BE1-851 Curve |  | M
|  | Curve Name |  | M, Moderately Inverse
|  | Drawing No. |  | 99-1369
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
0.3022 | 0.1284 | 1 | 0.5 | 0.028 | 3.7 | 5 | 9.8475
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | CO-7 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.4
|  |  | 1 | 0.8
|  |  | 2 | 1.7
|  |  | 3 | 2.5
|  |  | 4 | 3.3
|  |  | 5 | 4.3
|  |  | 6 | 5.3
|  |  | 7 | 6.1
|  |  | 8 | 7
|  |  | 9 | 8
|  |  | 10 | 9
|  |  | 11 | 9.8

## ABB CO-8
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-8
|  | BE1-851 Curve |  | I1
|  | Curve Name |  | I, Inverse Time
|  | Drawing No. |  | 99-1373
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
8.9341 | 0.17966 | 1 | 2.0938 | 0.028 | 5 | 5 | 9.986
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | CO-8 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.3
|  |  | 1 | 0.7
|  |  | 2 | 1.5
|  |  | 3 | 2.3
|  |  | 4 | 3.2
|  |  | 5 | 4
|  |  | 6 | 5
|  |  | 7 | 5.8
|  |  | 8 | 6.8
|  |  | 9 | 7.6
|  |  | 10 | 8.7
|  |  | 11 | 10

## ABB CO-9
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO -9
|  | BE1-851 Curve |  | V1
|  | Curve Name |  | V, Very Inverse
|  | Drawing No. |  | 99-1374
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
5.4678 | 0.10814 | 1 | 2.0469 | 0.028 | 3.1 | 5 | 9.6373
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | C0-9 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.3
|  |  | 1 | 0.7
|  |  | 2 | 1.4
|  |  | 3 | 2.1
|  |  | 4 | 3
|  |  | 5 | 3.9
|  |  | 6 | 4.8
|  |  | 7 | 5.7
|  |  | 8 | 6.7
|  |  | 9 | 7.8
|  |  | 10 | 8.7
|  |  | 11 | 9.6

## ABB CO-11
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | ABB CO-11
|  | BE1-851 Curve |  | E1
|  | Curve Name |  | E, Extremely Inverse
|  | Drawing No. |  | 99-1375
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
7.7624 | 0.02758 | 1 | 2.0938 | 0.028 | 3.15 | 5 | 10.2671
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | C0-11 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.3
|  |  | 1 | 0.7
|  |  | 2 | 1.5
|  |  | 3 | 2.4
|  |  | 4 | 3.2
|  |  | 5 | 4.2
|  |  | 6 | 5
|  |  | 7 | 5.7
|  |  | 8 | 6.6
|  |  | 9 | 7.8
|  |  | 10 | 8.5
|  |  | 11 | 10.3

## GE IAC-51
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | GE IAC-51
|  | BE1-851 Curve |  | I2
|  | Curve Name |  | I2, Inverse Time
|  | Drawing No. |  | 99-1597
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
0.2747 | 0.10426 | 1 | 0.4375 | 0.028 | 4 | 5 | 10.6481
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | IAC-51 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.6
|  |  | 1 | 1
|  |  | 2 | 1.9
|  |  | 3 | 2.7
|  |  | 4 | 3.7
|  |  | 5 | 4.8
|  |  | 6 | 5.7
|  |  | 7 | 6.8
|  |  | 8 | 8
|  |  | 9 | 9.3
|  |  | 10 | 10.6

## GE IAC-53
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | GE IAC-53
|  | BE1-851 Curve |  | V2
|  | Curve Name |  | V2, Very Inverse
|  | Drawing No. |  | 99-1596
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
4.4309 | 0.0991 | 1 | 1.9531 | 0.028 | 2.9 | 5 | 9.6102
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | IAC-53 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.4
|  |  | 1 | 0.8
|  |  | 2 | 1.6
|  |  | 3 | 2.4
|  |  | 4 | 3.4
|  |  | 5 | 4.3
|  |  | 6 | 5.1
|  |  | 7 | 6.3
|  |  | 8 | 7.2
|  |  | 9 | 8.4
|  |  | 10 | 9.6

## GE IAC-55
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | GE IAC-55
|  | BE1-851 Curve |  | S2
|  | Curve Name |  | S2, Short Inverse
|  | Drawing No. |  | 99-1595
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
0.0286 | 0.0208 | 1 | 0.9844 | 0.028 | 0.305 | 5 | 9.8301
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | IAC-55 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.2
|  |  | 1 | 1
|  |  | 2 | 2
|  |  | 3 | 3.1
|  |  | 4 | 4
|  |  | 5 | 4.9
|  |  | 6 | 6.1
|  |  | 7 | 7.2
|  |  | 8 | 8.1
|  |  | 9 | 8.9
|  |  | 10 | 9.8

## GE IAC-66
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | GE IAC-66
|  | BE1-851 Curve |  | L2
|  | Curve Name |  | L2, Long Inverse
|  | Drawing No. |  | 99-1594
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
2.3955 | 0 | 1 | 0.3125 | 0.028 | 40 | 5 | 10.906
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | IAC-66 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.4
|  |  | 1 | 0.9
|  |  | 2 | 1.8
|  |  | 3 | 2.7
|  |  | 4 | 3.9
|  |  | 5 | 4.9
|  |  | 6 | 6.3
|  |  | 7 | 7.2
|  |  | 8 | 8.5
|  |  | 9 | 9.7
|  |  | 10 | 10.9

## GE IAC-77
Basler Electric Time Overcurrent Characteristic Curve
|  | Equivalent to |  | GE IAC-77
|  | BE1-851 Curve |  | E2
|  | Curve Name |  | E2, Extremely Inverse
|  | Drawing No. |  | 99-1598
Equation
T=(A*D)/(M^N-C)+B*D+K
Where
Curve Constants |  |  |  |  | Time to Trip (Sec.) | Multiple of Tap | Time Dial
A | B | C | N | K | T | M | D
4.9883 | 0.0129 | 1 | 2.0469 | 0.028 | 2.05 | 5 | 9.8609
Basler Electric Equivalent Time Dial Calculator
Enter in the above table, "Time to Trip" and "Multiple of Tap"
from the Elecro-Mechanical Curve to get equivalent time dial setting.
Equivalent Time Dial Cross Reference Table
|  |  | IAC-77 | Basler
|  |  | Time Dial | Time Dial
|  |  | 0.5 | 0.5
|  |  | 1 | 1
|  |  | 2 | 1.9
|  |  | 3 | 2.7
|  |  | 4 | 3.5
|  |  | 5 | 4.3
|  |  | 6 | 5.2
|  |  | 7 | 6.2
|  |  | 8 | 7.4
|  |  | 9 | 8.2
|  |  | 10 | 9.9