型號: Avtron Model  K875A

Permanent Outdoor Resistive Load Bank 戶外 weatherproof 防水型負載器

for testing electrical power sources.  Suitable for installation and operation outdoors on roof, floor, or cement pad.

設計標準: Standards: The equipment covered by this specification shall be designed as it applies with the latest standard of NEMA, NEC, ISO and ANSI standards.

容量: Capacity:  Capable of providing 1000 KW at 480 Volts, 3 Phase, 60 Hz, 1202 Amps per Phase.

容許精度:Tolerance:  -0% to +5% at rated voltage.  Load Bank will not deliver less than 1000 KW at rated voltage.

負載最小仟瓦數: Load Steps:  Minimum 5 KW Load Step Resolution.  Branch circuit fuse protection provided for each load step.  保護熔絲: Fuses are 200K A.I.C. interrupting type.

電阻絲材質Load Elements:  Avtron Helidyne (材質Helically wound chromium alloy材質: 螺旋狀的鉻合金) Load Elements fully supported across its entire length within the air stream by segmented 陶瓷絕緣ceramic insulators with steel rod support. All exterior fasteners shall be stainless steel.

電阻絲設計必需可單獨取出以利維護保養Load elements shall be contained in multiple resistor cases or trays. Each can be removed in their entirety as a unit if service becomes necessary.

底部進風向上頂部排風型散熱冷卻風扇Cooling System:  Integrally mounted blower motor running from an internal/external power source of 480 Volts, 3 Phase, 60 Hz.風扇馬達需為屋外防雨型TEAO 或 TEFC 型.

風壓保護開關Air Fail:  A differential pressure switch 0.50” diameter is provided and is electrically interlocked with the load application controls to prevent load from being applied if the blower is not functioning.

市電失敗負載器自動卸載開關Auto Load Dump:  Provisions provided for remote load dump from a normally closed set of aux contacts from the transfer switch.  In the event of a utility failure, load will be removed.

提供數位顯示面板Metering:  Avtron Digital Power Metering Unit.  Instrumentation includes digital display of顯示功能包括: 3 Phase, Volts, Amps, Frequency and Kilowatts.

數位控制板19”包含控制顯示操作開關Controls:  Main Power on/off, Blower start/stop push buttons, master load on/off switch, and individual load step toggle switches for on/off application of resistive load segments.  Indicators include main power on, blower on, air failure. The controls will be supplied in a separate remote wall mount enclosure.

負載器俱備變壓器提供120V控制電源Control Power:   120V, 1 Phase, 60 Hz provided by integral 480V to 120V, single phase, control power transformer.

負載器構造Construction: Aluminized steel per ASTM A463, Vertical airflow, thermostatically controlled/heated relay compartment.

負載器出廠前電氣測試: All electrical circuits shall have a hipot test performed at twice rated voltage plus 1000VAC.

負載器外觀: The exterior of the load bank shall be painted with polyurethane enamel paint at a minimum 2 MILS dry film thickness with a spatter finish.

負載器尺寸重量K875A Size/Weight:  138”H x 60”D x 40"W., 1600 Pounds

提供兩套詳細操作手冊及負載器接線、控制、內部配置詳細圖面Two (2) sets of Instruction Manuals.